## Slide 1
NEED FOR ADAPTATION of POWER SYSTEMS & CONTROL SOLUTIONS
LED Airfield Lighting
October 20, 2015
IES ALC 2015
Notes: Indroduction:
BD doesn‘t just mean new market development but also setting up a long term roadmap.
To do this, analysis of todays system deficiencies needs to be done, based on this, a strategic plan for technology can be established.
Here I‘m talking about findings regarding power supply during recent implementations of LED lighting circuits with fixtures from various manufacturers .

## Slide 2: Airfield Lighting – Transition
Resistive Load
Non-linear Load
Resistive Load
Digitally-controlled Phase Cut
Sine Wave
Analog
?

## Slide 3: Current challenges of LED Airfield Lighting power supply
Series circuit are no longer of Resistive in nature
Performance of LED fixtures varies from manufacturer to manufacturer, this needs high effort in system design and supplier selection
Significant impact on Constant Current Regulators
Retrofitting into existing circuits pose significant challenges
Initially the only way to launch LED fixtures was to make them „Plug and play“ with existent technology
Notes: Due to non linear load from LEDs
Performance but also fail open!
High start up voltage
Different progression on light output...same dimming curve as incandecent is required

## Slide 4: Comparison of Waveform
Sinus Output Waveform
Phase Cut Output Waveform

## Slide 5: Crest Factor
Notes: High crest factor =low efficiency...comes from high start up voltage required by LEDs.
6.6 RMS mit led am Anfang
Unteres Bild: high Tap
Hoher peak Strom gibt hohe Spannung.
(FAA allows for max. Of 3.2)

## Slide 6: Challenges as System Integrator
Different manufacturers have different design approaches
Inter-brand uniformity of photometry is required for different applications
Distinguishing between LED Driver failure and actual LED failure
High Startup voltage requirements
Circuit stability issues
High start up timing/difference in startup timing
Significant time in fine tuning the system to meet required performance

## Slide 7: High Start Up Voltage – Our Observations
Instantaneous Voltage Vs Current for this LED
current
Brightness change
wave form for a passive load
Notes: It‘s required to overcome the Diode forward voltage to conduct.
with 130 degree conduction angle. Higher conduction angel = higher brightness

## Slide 8: High Start Up Voltage
Key Observations
If taping is according to calculated values, the set current could not be reached and the CCR trips as per regulatory requirement. The Voltage tap was increased step by step till the systems starts up.
The high tap setting of a phase cut CCR is necessary to satisfy the startup voltage requirement of LED fixtures but it causes a sub-optimal conduction angle of the phase cut CCR with high crest factor with high THD.
A very high tapping causes a sub-optimal conduction angle on a phase cut CCR causing bad PF
The input PF of the CCR reduces up to .6 if no active PF correction is not used for the CCR. (This is still a technical challenge and for sure a cost issue)
This reduces the efficiency of the circuit and does not provide the expected energy reduction by the replacement of a 45 W Halogen with a 11W LED fixture. This is not the case with Sine Wave Regulators since they actually handle over the saved power to the primary side.
The CCR capacity cannot be reduced even if the VA requirement for LED lamps at steady state is much lesser than for a Halogen fixture.
CCR
ASD
ASD
ASD
ASD
ASD
ASD
LCM
SCC
Test Setup Taxiway Centre Line Circuit – 60 Bi-direction Fixtures
Tap Setting
900V
11W (TXY Center)
7.5 W
Requires up to 5V start up voltage for the electronics
Notes: LCM: Lamp Control Master; SCC: Serial Circuit Coupler
Auch der Sinusregler benötigt die höhere Anzapfung. Das Problem der „high startup voltage“ muss also der Feuerhersteller lösen.
LED Manufacturer : Vendor 1 (Don’t have to provide the name here)
Fixture Type : Taxiway center line
Published wattage by Manufacturer : 11 W
CCR used: Tested on multiple CCRs from different vendors
Test setup : 60 bi-directional light fixtures
ASDs : Lights connected through 60 dual channel ASDs
Isolation transformer used : 100 W
Cable length : negligible (less than 200 m)
Max wattage requirement : Lights Wattage (at 11W) + ASD wattage + Iso TXRs losses + CCR losses
Voltage tapping as per calculation = 500 V
Result : Current not able to reach the set current and the CCR trips as per regulatory requirement.
Voltage tap increased step by step till the systems starts up.
The final tap setting at which the test setup starts working = 900 V
Partial Solution for the problem
Sine CCR. As the Sine CCR provides a constant crest factor with less THD at all output voltage levels, the efficiency is much better while using with LED fixtures.
However in case, the CCR capacity still have to be overrated approx. 3 times for satisfying the startup voltage.

## Slide 9: Trigger SCR v/s IGBT
SCR triggering
IGBT triggering

## Slide 10: ASD Communication (FSK)
Notes: FSK = frequency shift keying

## Slide 11: Circuit Stability
Key Observations
The circuit current oscillates heavily before CCR trips with I > I norm fault. So the Voltage tap was increased step by step till the system got stable.
The high tap setting of a phase cut CCR increased the over all inductance of the circuit from the CCR transformer, reducing the % variations by LED’s lamp fixtures switching loads making the control loop more stable.
To verify the above point, the voltage tapping of the CCR was reduced and an inductor(140 mH) was added to the circuit making it stable.
While retro fitting the LEDs in circuits with older CCRs, the tapping cannot be reduced even if the VA requirement for LED fixtures are much lesser making the overall system in-efficient.
At times a combination of high tapping and additional load can make the circuit stable. This causes additional work during the commissioning phase for fine tuning each circuit and testing for circuit stability.
CCR
ASD
ASD
ASD
ASD
ASD
ASD
LCM
SCC
Test Setup Touch Down Zone Circuit – 70 Bi-direction Fixtures
Tap Setting
1400V
20W (TDZ)
7.5 W
The non-linear/switching load characteristics of LEDs interferes with the CCRs regulation control loop.
Notes: LED Manufacturer : Vendor 2 (Don’t have to provide the name here)
Fixture Type : Touch down Zone fixture
Published wattage by Manufacturer : 20 W
CCR used: Tested on multiple CCRs from different vendors
Test setup : 70 fixtures
ASDs : Lights connected through 35 dual channel ASDs
Isolation transformer used : 100 W
Cable length : negligible (less than 200 m)
Max wattage requirement : Lights Wattage (at 20W) + ASD wattage + Iso TXRs losses + CCR losses
Voltage tapping as per calculation = 400 V
Observation: Circuit current oscillates heavily before CCR trips with I > I norm fault.
Voltage tap increased step by step till the system is stable.
The final tap setting at which the test setup starts working = 1400 V (approx.)
High Tapping means high Inductivity in the circuit
Reason: Results/Inference:
The high tap setting of a phase cut CCR increased the over all inductance of the circuit from the CCR transformer, reducing the % variations by LED’s lamp fixtures switching loads making the control loop more stable.
To verify the above point, the voltage tapping of the CCR was reduced and an inductor(140 mH) was added to the circuit making it stable.
While retro fitting LEDs in circuits with older CCRs, the tapping cannot be reduced even if the VA requirement for LED fixtures are much lesser making the overall system in-efficient.
At times a combination of high tapping and additional load need to be added to make the circuit stable. This causes additional work during the commissioning phase for fine tuning each circuit and testing for circuit stability.
Partial Solution for the problem
Configurable Control loop parameters for CCRs: One way of solving this problem without additional load and high tapping is to provide configurable control loop parameters for the CCRs to tune this in the field.
Even with tunable CCR control loop parameters, at certain combinations the circuit can be unstable as the traditional SCR based control does a cycle by cycle correction.
Solution to the problem
IGBT based CCRs with faster control loop for intra-cycle correction.

## Slide 12: High Start Up Timing
Key Observations
The ASD measures the current flowing into the lamp to detect a failure. LED light fixtures takes more time to draw current which is measurable enough. Only to be solve with tunable timing parameter in the ASD device.
LED light fixtures with electronics are difficult to ascertain lamp failure or driver failure. However, the importance for the operator is low since in any case, the fixture needs to be replaced.
CCR
ASD
ASD
ASD
ASD
ASD
ASD
LCM
LCM
Test Setup – Various Fixtures
7.5 W
The ASD detects the lamp as faulty.
Cannot Detect Lamp or Driver Failure
various power-ratings
Notes: LED Manufacturer : Vendor 3 (Don’t have to provide the name here)
Fixture Type : Various
Published wattage by Manufacturer : various
CCR used: Tested on multiple CCRs from different vendors
Light connected through Honeywell Addressable switch device.
Observation: The ASD detects the lamp as faulty.
Reason: The ASD measures the current flowing into the lamp to detect a failure. This particular light fixtures takes more time to draw current which is measurable enough.
Solution for the problem
Tunable timing parameter for ASD/fault detection devices for the lamp.

## Slide 13: Key Thoughts
Existing electrical infrastructure at airports are designed to work with linear loads
Most of the LED fixtures have switch mode power supply. For CCR it is an active load that changes with time, typical CCR regulation happens in 10ms steps, the full regulation sequence shall be completed in max. 500 ms
The interaction of an active load from LED fixtures and slow correction can cause heavy circuit oscillation
Retrofitting LED lamps to existing infrastructure is challenging and not energy efficient
IGBT Sinewave CCRs are still partial solution
Notes: IGBT: Insulated Gate Bipolar Transistor = is required for this kind of high power regulation
With today‘s power supplies, we don‘t utilize the full potential of LEDs

## Slide 14: Need for New Approach
Complete and holistic approach to address the requirements of modern airfield ground lighting
  Minimal systems with maximum intelligence
  Enable predictive maintenance regime and big data capability
  Reduced cost of installation, operation and maintenance
Robust and fast data communication instead complexity of addressable system
Power supply designed for luminars used - save low voltage circuits instead of high voltage
Today we try to mimic resistive loads to the CCR
LED Array and Power Supply designed to meet maximum useful lifetime of luminaires, addressing parametric changes and total failures
Notes: Points to make:
AGL is a safety critical infrastructure – we need a robust and reliable solution
LED fixtures are still seen as „power savers“ on their own, without realizing that the savings will only come with a tuned solution.
In order to get out the most benefits of new luminars, it is necessary to adopt the overall system infrastructure to the actual requirements of this luminars in order to get a seamless solution. It is not done with just replacing the light source.

## Slide 15: Questions?
Questions?
Thank you!
gerald.panhoelzl@honeywell.com +41 78 6110719